## Systematic SDS
Survey Data Sheet
Survey Number |  | INIS-FSS-052920-006
Date Surveyed |  | 2020-05-28
Survey Tech |  | J. Kallunki/J. Walther |  |  | Item Surveyed | General Exhaust West Plenum on the 8th Floor / Penthouse - Survey Unit HRT-11-13
Count Room Tech |  | J. Cuevas |  |  | Comments | Class 2 Final Status Survey (FSS). Static readings were taken with 43-93 probes. All corresponding smears were taken at same location as static for each survey location. Scans of all surfaces performed with 43-93 probes.
Date Counted |  | 5/29/20
Survey Unit |  | HRT-11-13 |  |  | Instrumentation
Building Material Background - cpm |  |  | Alpha | Beta | Gamma |  |  |  |  | Total Activity | [5 empty] | Removable Activity
Brick |  |  | 2 | 423 | [5 empty] | Alpha |  |  | Beta-Gamma |  |  | Alpha |  |  | Beta-Gamma
Concrete |  |  | 2 | 262 | 19 | Instrument Model |  |  |  | 2360/43-93 | [5 empty] | ASC-DP
Linoleum |  |  | 1 | 212 | 247480 | Instrument SN |  |  |  | 259730/PR374384 | [5 empty] | 0920930
Drywall |  |  | 1 | 194 | 2020-10-23 | Cal Due Date |  |  |  | 2021-03-11 | [5 empty] | 2021-02-18
Metal |  |  | 1 | 188 | N/A | Instrument Efficiency |  |  |  | 19.31% |  |  | 62% |  |  | 22.52% |  |  | 37.57%
Ceiling Tile |  |  | 2 | 307 | N/A | Surface Efficiency |  |  |  | 25% |  |  | 75% |  |  | 100% |  |  | 100%
Wood |  |  | 1 | 184 | N/A | Probe Correction Factor |  |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1
[5 empty] | 1 | Background Count Time (min) |  |  |  | 1 |  |  | 1 |  |  | 60 |  |  | 60
[5 empty] | 1 | Sample Count Time (min) |  |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1
[5 empty] | 5 | Instrument Background |  |  |  | 0 |  |  | 247 |  |  | 7 |  |  | 1589
[5 empty] | N/A | MDC |  |  |  | See Below
[5 empty] | Gamma | Total Activity | [9 empty] | Removable Activity
Note | *MDC & Net Activity displayed in dpm/100cm² |  |  |  |  | Alpha |  |  |  |  | Beta-Gamma |  |  |  |  | Alpha |  |  | Beta-Gamma
No | Description/Location |  |  |  | Gross CPM / mR/hr | Gross Counts | Bldg Material Bkg | MDC* | Net cpm | Net Activity* | Gross Counts | Bldg Material Bkg | MDC* | Net cpm | Net Activity* | Gross Counts | Net cpm | Net Activity* | Gross Counts | Net cpm | Net Activity*
1 | Floor |  |  |  |  | 0 | 1 |  |  |  | 357 | 188 |  |  |  | 0 |  |  | 39
| Floor |  |  |  |  | 1 | 1 |  |  |  | 333 | 188 |  |  |  | 0 |  |  | 33
| Floor |  |  |  |  | 0 | 1 |  |  |  | 248 | 188 |  |  |  | 0 |  |  | 33
| Floor |  |  |  |  | 2 | 1 |  |  |  | 229 | 188 |  |  |  | 0 |  |  | 26
| Ceiling |  |  |  |  | 0 | 1 |  |  |  | 362 | 188 |  |  |  | 0 |  |  | 43
| Ceiling |  |  |  |  | 3 | 1 |  |  |  | 289 | 188 |  |  |  | 0 |  |  | 61
| Ceiling |  |  |  |  | 1 | 1 |  |  |  | 273 | 188 |  |  |  | 0 |  |  | 30
| East Wall |  |  |  |  | 1 | 1 |  |  |  | 405 | 188 |  |  |  | 0 |  |  | 32
| East Wall |  |  |  |  | 2 | 1 |  |  |  | 272 | 188 |  |  |  | 0 |  |  | 39
| East Wall |  |  |  |  | 2 | 1 |  |  |  | 223 | 188 |  |  |  | 0 |  |  | 32
| East Wall |  |  |  |  | 1 | 1 |  |  |  | 259 | 188 |  |  |  | 0 |  |  | 35
| East Wall |  |  |  |  | 1 | 1 |  |  |  | 146 | 188 |  |  |  | 0 |  |  | 27
| East Wall |  |  |  |  | 1 | 1 |  |  |  | 213 | 188 |  |  |  | 1 |  |  | 31
| North Wall |  |  |  |  | 0 | 1 |  |  |  | 222 | 188 |  |  |  | 0 |  |  | 33
| West Wall |  |  |  |  | 1 | 1 |  |  |  | 199 | 188 |  |  |  | 0 |  |  | 32
| West Wall |  |  |  |  | 1 | 1 |  |  |  | 206 | 188 |  |  |  | 0 |  |  | 43
| West Wall |  |  |  |  | 1 | 1 |  |  |  | 221 | 188 |  |  |  | 0 |  |  | 29
| West Wall |  |  |  |  | 2 | 1 |  |  |  | 350 | 188 |  |  |  | 0 |  |  | 31
| West Wall |  |  |  |  | 3 | 1 |  |  |  | 323 | 188 |  |  |  | 0 |  |  | 35

## Systematic Map
SURVEY INFORMATION SHEETS
Survey No | INIS-FSS-052920-006
Survey Unit | HRT-11-13

## Judgmental SDS
Survey Data Sheet
Survey Number |  | INIS-FSS-052920-006
Date Surveyed |  | 2020-06-02
Survey Tech |  | J. Walther |  |  | Item Surveyed | General Exhaust West Plenum on the 8th Floor / Penthouse - Survey Unit HRT-11-13
Count Room Tech |  | J. Cuevas |  |  | Comments | Class 2 Final Status Survey (FSS). Static and smear measurements on each surface were taken at judgemental locations using Ludlum 43-93 probes.
Date Counted |  | 2020-06-02
Survey Unit |  | HRT-11-13 |  |  | Instrumentation
Building Material Background - cpm |  |  | Alpha | Beta | Gamma |  |  |  |  | Total Activity | [5 empty] | Removable Activity
Brick |  |  | 3 | 372 | [5 empty] | Alpha |  |  | Beta-Gamma |  |  | Alpha |  |  | Beta-Gamma
Concrete |  |  | 2 | 193 |  | Instrument Model |  |  |  | 2360/43-93 | [5 empty] | 3030
Linoleum |  |  | 0 | 152 |  | Instrument SN |  |  |  | 248145/PR389059 | [5 empty] | 271337
Drywall |  |  | 1 | 135 |  | Cal Due Date |  |  |  | 2020-11-18 | [5 empty] | 2021-03-04
Metal |  |  | 1 | 128 | N/A | Instrument Efficiency |  |  |  | 21.96% |  |  | 80% |  |  | 33.34% |  |  | 38.91%
Ceiling Tile |  |  | 2 | 260 | N/A | Surface Efficiency |  |  |  | 25% |  |  | 75% |  |  | 100% |  |  | 100%
Wood |  |  | 1 | 132 | N/A | Probe Correction Factor |  |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1
[6 empty] | Background Count Time (min) |  |  |  | 1 |  |  | 1 |  |  | 60 |  |  | 60
[6 empty] | Sample Count Time (min) |  |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1
[6 empty] | Instrument Background |  |  |  | 2 |  |  | 251 |  |  | 2 |  |  | 2140
[5 empty] | N/A | MDC |  |  |  | See Below
[5 empty] | Gamma | Total Activity | [9 empty] | Removable Activity
Note | *MDC & Net Activity displayed in dpm/100cm² |  |  |  |  | Alpha |  |  |  |  | Beta-Gamma |  |  |  |  | Alpha |  |  | Beta-Gamma
No | Description/Location |  |  |  | Gross CPM / mR/hr | Gross Counts | Bldg Material Bkg | MDC* | Net cpm | Net Activity* | Gross Counts | Bldg Material Bkg | MDC* | Net cpm | Net Activity* | Gross Counts | Net cpm | Net Activity* | Gross Counts | Net cpm | Net Activity*
20 | West wall South Louvers South |  |  |  |  | 1 | 1 |  |  |  | 1533 | 128 |  |  |  | 1 |  |  | 49
21 | West wall South Louvers top |  |  |  |  | 1 | 1 |  |  |  | 1255 | 128 |  |  |  | 1 |  |  | 45
23 | Floor |  |  |  |  | 0 | 1 |  |  |  | 1792 | 128 |  |  |  | 0 |  |  | 90

## Judgmental SDS (2)
Survey Data Sheet
Survey Number |  | INIS-FSS-052920-006
Date Surveyed |  | 2020-06-02
Survey Tech |  | J. Kallunki |  |  | Item Surveyed | General Exhaust West Plenum on the 8th Floor / Penthouse - Survey Unit HRT-11-13
Count Room Tech |  | J. Cuevas |  |  | Comments | Class 2 Final Status Survey (FSS). Static and smear measurements on each surface were taken at judgemental locations using Ludlum 43-93 probes.
Date Counted |  | 2020-06-02
Survey Unit |  | HRT-11-13 |  |  | Instrumentation
Building Material Background - cpm |  |  | Alpha | Beta | Gamma |  |  |  |  | Total Activity | [5 empty] | Removable Activity
Brick |  |  | 2 | 423 | [5 empty] | Alpha |  |  | Beta-Gamma |  |  | Alpha |  |  | Beta-Gamma
Concrete |  |  | 2 | 262 |  | Instrument Model |  |  |  | 2360/43-93 | [5 empty] | 3030
Linoleum |  |  | 1 | 212 |  | Instrument SN |  |  |  | 259730/PR374384 | [5 empty] | 271337
Drywall |  |  | 1 | 194 |  | Cal Due Date |  |  |  | 2021-03-11 | [5 empty] | 2021-03-04
Metal |  |  | 1 | 188 | N/A | Instrument Efficiency |  |  |  | 19.31% |  |  | 62% |  |  | 33.34% |  |  | 38.91%
Ceiling Tile |  |  | 2 | 307 | N/A | Surface Efficiency |  |  |  | 25% |  |  | 75% |  |  | 100% |  |  | 100%
Wood |  |  | 1 | 184 | N/A | Probe Correction Factor |  |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1
[6 empty] | Background Count Time (min) |  |  |  | 1 |  |  | 1 |  |  | 60 |  |  | 60
[6 empty] | Sample Count Time (min) |  |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1
[6 empty] | Instrument Background |  |  |  | 1 |  |  | 259 |  |  | 2 |  |  | 2140
[5 empty] | N/A | MDC |  |  |  | See Below
[5 empty] | Gamma | Total Activity | [9 empty] | Removable Activity
Note | *MDC & Net Activity displayed in dpm/100cm² |  |  |  |  | Alpha |  |  |  |  | Beta-Gamma |  |  |  |  | Alpha |  |  | Beta-Gamma
No | Description/Location |  |  |  | Gross CPM / mR/hr | Gross Counts | Bldg Material Bkg | MDC* | Net cpm | Net Activity* | Gross Counts | Bldg Material Bkg | MDC* | Net cpm | Net Activity* | Gross Counts | Net cpm | Net Activity* | Gross Counts | Net cpm | Net Activity*
22 | East wall |  |  |  |  | 0 | 1 |  |  |  | 1281 | 188 |  |  |  | 0 |  |  | 44

## Judgmental Map
SURVEY INFORMATION SHEETS
Survey No | INIS-FSS-052920-006
Survey Unit | HRT-11-13

## QC
Survey Data Sheet
Survey Number |  | INIS-FSS-052920-006
Date Surveyed |  | 2020-06-18
Survey Tech |  | M. Renderos |  |  | Item Surveyed | General Exhaust West Plenum on the 8th Floor / Penthouse - Survey Unit HRT-11-13
Count Room Tech |  | J. Cuevas |  |  | Comments | Quality control duplicates collected from at least 20% of predetermined and judgmental survey locations. Duplicate locations were chosen randomly and surveyed by a different technician using a different instrument than those originally used.
Date Counted |  | 2020-06-18
Survey Unit |  | HRT-11-13 |  |  | Instrumentation
Building Material Background - cpm |  |  | Alpha | Beta | Gamma |  |  |  |  | Total Activity | [5 empty] | Removable Activity
Brick |  |  | 3 | 366 | [5 empty] | Alpha |  |  | Beta-Gamma |  |  | Alpha |  |  | Beta-Gamma
Concrete |  |  | 2 | 195 |  | Instrument Model |  |  |  | 2360/43-93 | [5 empty] | ASC-DP
Linoleum |  |  | 1 | 161 |  | Instrument SN |  |  |  | 227400/PR299616 | [5 empty] | 0920930
Drywall |  |  | 1 | 138 |  | Cal Due Date |  |  |  | 2021-03-09 | [5 empty] | 2021-02-18
Metal |  |  | 0 | 132 | N/A | Instrument Efficiency |  |  |  | 19.54% |  |  | 74% |  |  | 22.52% |  |  | 37.57%
Ceiling Tile |  |  | 2 | 255 | N/A | Surface Efficiency |  |  |  | 25% |  |  | 75% |  |  | 100% |  |  | 100%
Wood |  |  | 0 | 138 | N/A | Probe Correction Factor |  |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1
Glass |  |  | N/A | N/A |  | Background Count Time (min) |  |  |  | 1 |  |  | 1 |  |  | 60 |  |  | 60
[6 empty] | Sample Count Time (min) |  |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1
[6 empty] | Instrument Background |  |  |  | 2 |  |  | 201 |  |  | 8 |  |  | 1675
[5 empty] | N/A | MDC |  |  |  | See Below
[5 empty] | Gamma | Total Activity | [9 empty] | Removable Activity
Note | *MDC & Net Activity displayed in dpm/100cm² |  |  |  |  | Alpha |  |  |  |  | Beta-Gamma |  |  |  |  | Alpha |  |  | Beta-Gamma
No | Description/Location |  |  |  | Gross CPM / mR/hr | Gross Counts | Bldg Material Bkg | MDC* | Net cpm | Net Activity* | Gross Counts | Bldg Material Bkg | MDC* | Net cpm | Net Activity* | Gross Counts | Net cpm | Net Activity* | Gross Counts | Net cpm | Net Activity*
24 | QC of location #3 |  |  |  |  | 0 | 0 |  |  |  | 254 | 132 |  |  |  | 0 |  |  | 27
25 | QC of location #7 |  |  |  |  | 0 | 0 |  |  |  | 212 | 132 |  |  |  | 0 |  |  | 36
26 | QC of location #8 |  |  |  |  | 0 | 0 |  |  |  | 319 | 132 |  |  |  | 0 |  |  | 33
27 | QC of location #16 |  |  |  |  | 1 | 0 |  |  |  | 173 | 132 |  |  |  | 0 |  |  | 31
28 | QC of location #23 |  |  |  |  | 0 | 0 |  |  |  | 1822 | 132 |  |  |  | 0 |  |  | 26

## Picture
Survey Information Sheet
Static readings were taken with 43-93 probes. All corresponding smears were taken at same location as static for each survey location. Scans of all surfaces performed with 43-93 probes.
Survey No |  | INIS-FSS-052920-006
Survey Unit |  | HRT-11-13

## Picture (2)
Survey Information Sheet
Static readings were taken with 43-93 probes. All corresponding smears were taken at same location as static for each survey location. Scans of all surfaces performed with 43-93 probes.
Survey No |  | INIS-FSS-052920-006
Survey Unit |  | HRT-11-13

## Picture (3)
Survey Information Sheet
Static readings were taken with 43-93 probes. All corresponding smears were taken at same location as static for each survey location. Scans of all surfaces performed with 43-93 probes.
Survey No |  | INIS-FSS-052920-006
Survey Unit |  | HRT-11-13

## Picture (4)
Survey Information Sheet
Static readings were taken with 43-93 probes. All corresponding smears were taken at same location as static for each survey location. Scans of all surfaces performed with 43-93 probes.
Survey No |  | INIS-FSS-052920-006
Survey Unit |  | HRT-11-13

## Picture (5)
Survey Information Sheet
Static readings were taken with 43-93 probes. All corresponding smears were taken at same location as static for each survey location. Scans of all surfaces performed with 43-93 probes.
Survey No |  | INIS-FSS-052920-006
Survey Unit |  | HRT-11-13

## Picture (6)
Survey Information Sheet
Static readings were taken with 43-93 probes. All corresponding smears were taken at same location as static for each survey location. Scans of all surfaces performed with 43-93 probes.
Survey No |  | INIS-FSS-052920-006
Survey Unit |  | HRT-11-13