## Survey
Survey Number |  | INIS-021820-1276
Date Performed |  | 2020-02-17
Survey Tech |  | M. Renderos
Count Room Tech |  | P. Ray |  |  | Item Surveyed |  | Room 220E ceiling, pre-decontamination
Date Counted |  | 2/18/2020 |  |  | Comments |  | 100% scan of all accessible areas. Smears/static counts taken at locations of highest activities. Area divided into grids (1-10). Material composition of scan area was concrete.
Survey Type |  | Characterization
Level Of Posting |  | CA |  |  | Instrumentation
Building Material Background - cpm |  |  | Alpha | Beta | Gamma | [5 empty] | Total Activity | [5 empty] | Removable Activity
Brick |  |  | 3 | 389.88 | Dose | CPM |  |  |  |  | Alpha |  |  | Beta-Gamma |  |  | Alpha |  |  | Beta-Gamma
Concrete |  |  | 2 | 223.0567 |  |  | Instrument Model |  |  |  | 2360/43-93 | [5 empty] | 2929/43-10-1
Linoleum |  |  | 1 | 182.55 |  |  | Instrument SN |  |  |  | 225238/PR294127 | [5 empty] | 185266/PR194717
Drywall |  |  | 1 | 165.0167 |  |  | Cal Due Date |  |  |  | 2020-10-30 | [5 empty] | 2021-01-22
Metal |  |  | 1 | 158.5767 | N/A | N/A | Instrument Efficiency |  |  |  | 20.63% |  |  | 35.43% |  |  | 35.57% |  |  | 40.71%
Ceiling Tile |  |  | 2 | 281 | N/A | N/A | Probe Correction Factor |  |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1
Wood |  |  | 1 | 160 |  |  | Background Count Time (min) |  |  |  | 1 |  |  | 1 |  |  | 60 |  |  | 60
[7 empty] | Sample Count Time (min) |  |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1
[7 empty] | Instrument Background |  |  |  | 0 |  |  | 319 |  |  | 7 |  |  | 2143
[5 empty] | N/A | N/A | MDC |  |  |  | See Below
[5 empty] | Gamma |  | Total Activity | [9 empty] | Removable Activity
Note | *MDC & Net Activity displayed in dpm/100cm² |  |  |  | Dose | CPM | Alpha |  |  |  |  | Beta-Gamma |  |  |  |  | Alpha |  |  | Beta-Gamma
No | Description/Location |  |  |  | µR/hr | cpm | Gross Counts | Bldg Material Bkg | MDC* | Net cpm | Net Activity* | Gross Counts | Bldg Material Bkg | MDC* | Net cpm | Net Activity* | Gross Counts | Net cpm | Net Activity* | Gross Counts | Net cpm | Net Activity*
1 | Ceiling (grid #1) | [5 empty] | 0 | 2 |  |  |  | 405 | 223 |  |  |  | 0 |  |  | 42
2 | Ceiling (grid #2) | [5 empty] | 0 | 2 |  |  |  | 407 | 223 |  |  |  | 0 |  |  | 47
3 | Ceiling (grid #3) | [5 empty] | 0 | 2 |  |  |  | 342 | 223 |  |  |  | 0 |  |  | 36
4 | Ceiling (grid #4) | [5 empty] | 0 | 2 |  |  |  | 310 | 223 |  |  |  | 0 |  |  | 40
5 | Ceiling (grid #5) | [5 empty] | 2 | 2 |  |  |  | 389 | 223 |  |  |  | 0 |  |  | 38
6 | Ceiling (grid #6) | [5 empty] | 0 | 2 |  |  |  | 333 | 223 |  |  |  | 0 |  |  | 28
7 | Ceiling (grid #7) | [5 empty] | 0 | 2 |  |  |  | 397 | 223 |  |  |  | 0 |  |  | 38
8 | Ceiling (grid #8) | [5 empty] | 0 | 2 |  |  |  | 610 | 223 |  |  |  | 1 |  |  | 36
9 | Ceiling (beam) (grid #9) | [5 empty] | 0 | 2 |  |  |  | 301 | 223 |  |  |  | 0 |  |  | 48
10 | Ceiling (beam) (grid #10) | [5 empty] | 0 | 2 |  |  |  | 389 | 223 |  |  |  | 0 |  |  | 43

## Map
Survey No | INIS-021820-1276
Date | 2020-02-17
Survey Tech | M. Renderos
Count Room Tech | P. Ray
Date Counted | 2020-02-18
Survey Type | Characterization
Level of Posting | CA
Comments

## Map (2)
Survey No | INIS-021820-1276
Date | 2020-02-17
Survey Tech | M. Renderos
Count Room Tech | P. Ray
Date Counted | 2020-02-18
Survey Type | Characterization
Level of Posting | CA
Comments